## Sheet1
Singapore Changi SIN T2
Form No.
[5 empty] | Fire Shutter Door Installation Inspection Report | [13 empty] | Revision No. | 01
[19 empty] | Page No | 1/1
Location |  | Area: | [10 empty] | Gridline: |  |  |  | Floor No/ Level
Date
Drawing No : | [12 empty] | Rev. No :
System : | [12 empty] | Subsystem :
| Clear opening width/height | Shutter box Secured, level & aligned | Guide rail Secured, level & aligned | Drive chain tension Adequate | Check Motor type: Single phase/Three phase | Isolator connection: Single phase/Three phase | Emergency power supply Emergency power supply available | Fire alarm connection: Voltage free signal Normally Open voltage free contacts | Fire alarm connection: 24VDC signal 24VDC, 400mA, Normally Open contacts | Push button Open, stop & close function | Hand chain Open & close function | Thermal fusible link Close when fuse detached | Fire alarm Close when fire alarm signal triggered | Overall operation Smooth | Overall condition Without dents & scratches | Upper Limit Switch installed and tested | Lower Limit Switch installed and tested
Inspected by | [7 empty] | Name and Signature | [9 empty] | Date
Witnessed by | [7 empty] | Name and Signature | [9 empty] | Date
[8 empty] | Name and Signature | [9 empty] | Date